## Slide 1: Rectifiers
2. Fully controlled rectifiers
line frequency ac is converted into variable voltage dc (uses controllable devices like SCRs, IGBT)
3. Half controlled converters
line frequency ac is converted into variable voltage dc (uses both uncontrollable and controllable devices)
Classification of Rectifiers
1. Uncontrolled rectifiers
line frequency ac is converted into fixed voltage dc.
(uses uncontrollable devices like diodes)

## Slide 2: Uncontrolled and Halfcontrolled Converters
average output voltage is always positive.
Power flow is from ac source to dc load
Unidirectional converters
operating points lie in the first quadrant of Average voltage Vd - Average current Id Plane
Single quadrant converters

## Slide 3: Uncontrolled Rectifiers
APPLICATIONS
Switching power supplies
ac motor drives
dc motor drives
battery chargers
electrochemical processes
HVDC Transmission

## Slide 4: Single phase Half wave rectifier - R load
π -2π D1 is off
id (ωt)= 0,
Vd (ωt)= 0
is(ωt)=0,
vD1 (ωt)=
vd
vd
Vs = Vmsinωt =√2Vssinωt
Vs – RMS value of source voltage
0 - π D1 conducts.
vd(ωt) =
id(ωt) =
Diode voltage vD1(ωt) = 0
vs(ωt)
vd(ωt) /R =
is(ωt)
vs(ωt)
id

## Slide 5: Performance parameters
Average value of output voltage Vdavg
Vdavg =
=
=
Average load current Idavg=
Peak load current =
Peak current rating of diode =
= Average current rating of diode

## Slide 6
RMS load voltage VdRMS
RMS load current IdRMS =
Load current Form factor =
RMS source current IsRMS =

## Slide 7
DC power delivered to the load Pdc = Vdavg x Idavg
DC power delivered /Transformer power rating
= Pdc / (Vs × IdRMS) =
Power rating of transformer must be greater by 1/.29 (=3.5) times the dc load power rating
29%
Transformer Utility factor TUF
If transformer RMS current rating is same as Idrms , then
TUF =

## Slide 8
Rectifier efficiency η
= dc side load power/(ac load power + rectifier loss)
Rf ----forward resistance of diode

## Slide 9
Ripple factor γ
= RMS value of ripple content in load voltage / Vdavg
Input source pf =
=
1.21

## Slide 10
Peak Inverse voltage PIV
Maximum instantaneous voltage that appears across the diode during the blocking state
=

## Slide 11: Single Phase Half wave uncontrolled Rectifier with R-L Load
id(0) =
0 ,
During positive half cycle diode is on
id
(did/dt) / t=0
= 0

## Slide 12
qqq
VL(t) =L (did/dt) =
= Vd(t) - VR(t

## Slide 13
0-t3
Area A = Area B

## Slide 14: R-L load with free wheeling diode
The effect of this diode is to prevent a negative voltage appearing across the load.
At t =Π/ω the current from D1 is transferred to Dm and this process is called commutation of diodes.
Continuity of the load current depends on its time constant τ = ωL/R.
Vs , i0, vR, vL, vD1, vdm
Average voltage (and current) can be increased by adding a freewheeling diode Dm .

## Slide 15: L-E load (dc motor with back emf)
• Diode is forward biased when Vs ≥ Ed
At ωt = ωt1 = α; vs = Ed
For ωt ≥ ωt1, D1 is on, Vdiode = 0
√2Vssin ω t =
Ldi/dt + Ed
i(t) =
At ωt = α i = 0
√2Vssin α = Ed
√2Vssin α = Ldi/dt + Ed
di/dt /ωt = α =(√2Vssin α –Ed)/L
=0
vL = vs - Ed
vdiode = vs - Ed

## Slide 16
• Current continues to flows for a while even after the input voltage has gone below the dc back-emf
t3 → 2π/ω
i = 0
di/dt = 0, vL = 0
Vdiode = vs-Ed

## Slide 17: Battery charging circuit
For Vs > E, diode D1 conducts.
The charging current i0(t)
D1 is turned off when io(t)=0 at β = (∏-α)

## Slide 18
Performance parameters
Average charging current I0avg
Series connected resistance R =
RMS value of Charging current I0RMS2

## Slide 19
PR = I0RMS 2 × R
Rectifier efficiency =
Power delivered to battery / total input power
Peak inverse voltage of diode=
Power delivered to the battery
Pdc = E × I0avg
Power rating of resistance R,

## Slide 20
A battery has a voltage of E=12V and capacity 100Wh. The average charging current should be Idc =5A. The primary input voltage is Vp =120V , 50Hz and the transformer has a turns ratio of 2:1.
Calculate
(a) conduction angle δ of the diode.
(b) current limiting resistor R
(c) power rating PR of R (d) charging time
(e) the rectifier η and (f) PIV of diode

## Slide 21
Secondary voltage =
α =
Conduction angle δ=
Average charging current = Idc =
R =
Power rating of resistor =
IoRMS2 R =
Power delivered to the battery =
E Idc =
η =
PIV =

## Slide 22: Single phase Fullwave Bridge rectifiers

## Slide 23
0 - ∏
vs is positive
D1,D2 forward biased
Current path is
Vs, D1, load, D2
Load voltage vd =
vs
Load current id =
vd/R
Source current is =
id
Source inductance Ls = 0, Load is pure resistance

## Slide 24
∏ - 2 ∏
Vs is negative
D3,D4 forward biased
Current path is
vs, D3, load, D4
vd =
-vs
id =
vd/R
is =
-id

## Slide 25: Performance parameters
Average load voltage Vdavg
Average load current Idavg
RMS load voltage VdRMS
RMS load current IdRMS = Vs/R

## Slide 26
Peak load current =
DC power delivered to the load
Transformer utility factor
PIV
Ripple factor =

## Slide 27: Source inductance Ls = 0, Load is R-L
id(ωt) /t=0 = + I0
is
0 - π
vs is positive,
D1,D2 forward biased
vd = vs ,
id(ω t) =
              is(ω t) = id(ω t)
-

## Slide 28: Source inductance Ls = 0, Load is R-L
id(ωt) / ωt = π = + I0
is
π - 2 π
vs is negative,
D3,D4 forward biased
vd = - vs ,
id(ω t) =
              is(ω t) = id(ω t)

## Slide 29: Ls = 0, Load is highly inductive so that id is constant at Id ωL»R
0 - ∏
vs is positive
D1,D2 forward
biased
vd = vs
id = Id
is = +Id
vD1 =

## Slide 30: Ls = 0, Load is highly inductive so that id is constant at Id
∏ -2 ∏
vs is negative
D3,D4 forward biased
vd = -vs
Id = Id
is = -Id
vD1 =
Average output voltage Vdavg =
=0.9Vs
ωL»R

## Slide 31: Source inductance is zero. Hence transition from positive to negative value of source current is instantaneous.
0
0

## Slide 32
RMS value of fundamental component of input current
Is1

## Slide 33
RMS value of nth harmonic of source current isn
RMS value of total source current Is =
THD of source current
Displacement factor of source current DF =
48.4%
Id
cosφ1=
1

## Slide 34: Harmonic components of Source Current
Source current and fundamental component
Harmonic components of Is

## Slide 35: AC source side Power factor = Actual power / Apparent power
Actual power

## Slide 36
Apparent power = Vs Is
Power Factor =
= Is1 / Is =
Peak current rating of diode =
= Id
RMS current rating of diode =
= Id
PIV of diode =
Vm

## Slide 37: Effect of source inductance Ls
+ VLs -
Due to source inductance the transition of ac side current from +Id to –Id is not instantaneous
A finite time interval is required for the transition of current from outgoing diodes to incoming diodes.
This time interval is called current commutation period µ.

## Slide 38
During the commutation
interval µ, all four diodes conduct.
Vd = 0
Drop in the inductance vLs
dis =
+ VLs -

## Slide 39
During the interval 0 to μ, is varies
from –Id to +Id
commutation interval µ =

## Slide 40
Average voltage Vdavg =
Average output voltage is reduced by

## Slide 41
Large values of current or/and source Inductance result in larger value of µ and make average voltage zero.
Vdavg
Id
Slope = - 2ωLs/π
Vdavg=0
µ=0
µ= π
Vdavg

## Slide 42
1. A single phase uncontrolled bridge rectifier connected to a 120V ac source supplies a constant load current of 10A.
  a. If Ls =0, find average output voltage and average output power. Plot vd and is.
  b. If Ls =5mH, find average output voltage and average output power and overlap angle.
Plot vd and is
2. Repeat the above question if input ac source is of square wave with an amplitude of 200V

## Slide 43: Bridge Rectifier with R-L-E load
Continuous current mode
id
id

## Slide 44
0 - ∏ D1 and D2 conduct.
is reverses instantaneously from –I0 to +I0
vd = vs
At ωt = π, id = I0
A1 =
id
id =

## Slide 45
id
id
id

## Slide 46: Discontinuous current mode
The diode starts to conduct at ωt = α
id
id
id
id

## Slide 47
β can found from the above relation.
id

## Slide 48: Diode Bridge rectifier with a Capacitor Filter (approximately constant potential at dc load side)
The previously charged capacitor filters the rectified voltage to make vd smooth.
This voltage is used as the input for inverter or dc-dc converter
iR = vd/R is the current through load resistor.
id = ic + iR
iR
ic

## Slide 49
t1 = θ1/ω and t4 = θ4/ω
t1 < t < t4
vs = Rs id + Ls did/dt + vd
id = Cd dvd/dt + vd/Rload

## Slide 50
t4 < t < t1+T/2 All Diodes are off
Cd dvd/dt = - vd/Rload
dvd/dt = - vd/ Cd Rload
vd (t) =
vd (t4) e-(t-t4) Cd Rload

## Slide 51: Course Outcome
CO1:Acquire knowledge about analysis and design of various types of DC Chopper circuits
CO2: Acquire knowledge about harmonic analysis and filter circuit design of uncontrolled rectifiers
CO3: Acquire knowledge about various types of controlled rectifiers
CO4: Acquire knowledge about various PWM techniques of 2-level DC to AC converters
CO5: Acquire knowledge about analysis of multilevel inverters with advanced PWM techniques

## Slide 52: Effect of diode rectifier on utility voltage & Current
Line current distortion
Source current deviates significantly from the sinusoidal waveform.
Line voltage distortion
Distortion in the line current results in the distortion of line voltage waveform.

## Slide 53
PCC- point of common coupling where other loads and power electronic load are connected
Vpcc Voltage across the PE equipment and other loads at the point of common coupling
Ls1 – Inductance of the utility side
Ls2- Inductance due to the power electronic equipment
Rs-represents the diode resistance

## Slide 54
Source current is
Distortion in voltage at PCC due to harmonics in line current

## Slide 55
Voltage available at the point of common coupling is highly deviated from the ideal sine waveform
This is usually referred to voltage pollution in power system
This is one of the reasons of power quality problems

## Slide 56: Effect of Single phase rectifiers on the neutral current in 3Ф 4 wire systems
When all the 3 phases are loaded equally or balanced, neutral current in = 0.
When single phase rectifiers are connected as load to 3Ф , in ≠ 0
Consider identical rectifiers connected between each phase and neutral (balanced load condition)

## Slide 57
Phase a current
ia
k=1,2,3,….

## Slide 58
Sum of the three phase fundamental components and non-triplen harmonics is zero.
ia1 + ib1 + ic1 = 0
        Neglecting all higher order harmonics,
Thus, neutral wire carries 3 times 3rd harmonic current flowing through a phase
neutral current is almost equal to or greater than the fundamental line current.
Neutral current iN = ia + ib + ic
        iN = ia3 + ib3 + ic3
        = 3 ia3 ≈ia1

## Slide 59: Neutral current